# EFFECTIVE February 22,  2021 AND SUPERSEDES ALL PREVIOUS VERSIONS.

SECTION 07 27 00

MECHANICALLY ATTACHED AIR AND WEATHER BARRIER

SIGA MAJVEST® 200

(Specifier Note: This specification includes materials and installation procedures for SIGA Majvest 200, a mechanically attached water-resistive, vapor permeable and air barrier sheet membrane, used in commercial and residential applications. SIGA Majvest 200 is specifically designed for above grade, vertical wall surfaces where the wall assembly may consist of any of the following: exterior gypsum sheathing, exterior plywood sheathing, oriented strand board (OSB) sheathing, stud walls with no sheathing, and masonry.

This specification, prepared in CSI three (3) part format, should be adapted to suit the requirements of the individual project and be included as a separate Section under Division 07 - Thermal and Moisture Protection.

This document is a reference for the recommended installation procedures of the products/assembly described. Although this specification Section follows the recommendations of the Construction Specifications Institute (CSI), Manual of Practice including Master Format, Section Format, and Page Format, it is the discretion of the project specification author to use the information within as a whole, or in part, to set a minimum standard of performance for specified products/assembly on a project specific basis. Update “[project specific]” notes and coordinate as required.

This document includes notes to assist the architect/specification writer. A SIGA “Specifier Note” will always immediately precede the text to which it is referring. This Section serves as a guideline only; modify to meet specific project requirements.

Delete “Specifier Note” Sections in the final copy of the specification).

(Specifier Note: For wall systems anticipating prefabrication and installation of air barrier as a panelized design: contact SIGA applications advisor for assistance and consult the SIGA Manual www.siga.swiss).

----------------------------------------------------------------------------------------------------

GENERAL

GENERAL REQUIREMENTS

The General Conditions, Supplementary Conditions, Instructions to Bidders, and Division 01- General Requirements shall be read in conjunction with and govern this Section.

This Specification Section should be read by all parties concerned. The contractor is responsible to make clear to the installing subcontractor the extent of their work.

This Section specifies the requirements for the supply and installation of the elements required for vapor permeable air barrier membranes.

SECTION INCLUDES

This Section includes requirements for supplying labor, materials, tools, and equipment to complete the work as shown on the drawings architectural division as specified herein including, but not limited to, the following:

Mechanically attached Weather resistive and air barrier (SIGA® Majvest 200).

Accessories:

  - Flashing Tapes (SIGA Wigluv®, SIGA Fentrim® 430 grey, SIGA Fentrim 230 grey, SIGA Fentrim IS 20).

  - Fasteners.

  - Adhesive/Primer (SIGA Dockskin® 100).

  - Sealant (SIGA Meltell® 300).

- Note to Specifier:  Carefully and completely edit "WORK SPECIFIED IN OTHER SECTIONS" below to coordinate with other sections being included in the project manual.

RELATED SECTIONS

(Specifier Note: Carefully and completely edit " RELATED SECTIONS" below to coordinate with other sections being included in the project manual).

Section 07 25 00 – Weather Barriers.

Section 07 50 00 - Membrane Roofing; requirement for coordination with sequencing of membrane roofing; requirement to seal roof membrane to wall air barrier.

Section 07 65 00 – Flexible Flashing tapes.

Section 07 92 00 – Joint Sealant

REFERENCE

ASTM International (ASTM):

ASTM D882 - Test Method for Tensile Properties of Thin Plastic Sheeting.

ASTM D1970 - Specification for Self-Adhering Polymer Modified Bituminous Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection.

ASTM D3330 - Test Method for Peel Adhesion of Pressure-Sensitive Tape.

ASTM D5034 -  Test Method for Breaking Strength and Elongation of Textile Fabrics.

ASTM E84 - Test Method for Surface Burning Characteristics of Building Materials.

ASTM E96 - Test Methods for Water Vapor Transmission of Materials.

ASTM E283 - Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

ASTM E330 - Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference.

ASTM E2178 - Test Method for Air Permeance of Building Materials.

ASTM E2357 - Test Method for Determining Air Leakage of Air Barrier Assemblies.

ASTM E2556/E2556M - Standard Specification for Vapor Permeable Flexible Sheet Water-Resistive Barriers Intended for Mechanical Attachment.

American Association of Textile Chemists and Colorists (AATCC): AATCC 127 - Test Method for Water Resistance: Hydrostatic Pressure Test.

American Architectural Manufacturers Association (AAMA).

AAMA 711-13 - Specification for Self Adhering Flashing Used for Installation of Exterior Wall Fenestration Products.

Standards Council of Canada.

CAN/ULC-S741:2008-R2016, Standard for Air Barrier Materials – Specifications.

CAN/ULC-S742-11, Standard for Air Barrier Assemblies – Specifications.

SUBMITTALS

Refer to Section [01 33 00 Submittal Procedures] [insert section number and title].

Product Data: Submit manufacturers’ current product data sheets, details and installation instructions for the water-resistive vapor permeable air barrier and drainage matrix membrane components and accessories.

Manufacturer Instructions: Submit manufacturer’s written installation instructions.

QUALITY ASSURANCE

Qualifications.

Installer shall have experience with installation of commercial sheet good air barrier assemblies.

Installation shall be in accordance with air barrier manufacturer’s installation guidelines and recommendations.

Source Limitations: Provide air and weather barrier, and accessory materials produced by single manufacturer.

Whenever possible, installer shall undergo an onsite SIGA installation training before the installation of SIGA products begin. Contact SIGA to set up a free installation training.

Compliance with Standards: Products shall meet or exceed the requirements of AATCC 127, ASTM D882, ASTM E84, ASTM E96, ASTM E2178, CAN/ULC S741-08, CAN/ULC-S742-11, ASTM E2357, ASTM E330, ASTM D5034, ASTM D1970, and ASTM D3330.

Mock-Up: Install a mock-up using approved air barrier system including membrane, flashing, joint and detailing tape and related air barrier accessories according to air barrier manufacturer’s current printed instructions and recommendations.

Mock-up Size: [10 feet by 10 feet] [insert size], in a location on the building.

Mock-up Substrate: Match wall assembly construction, including window opening and typical trough wall penetrations.

Mock-up may remain as part of the work.

Arrange for manufacturer’s designated representative prior to air barrier system installation, to perform required mock-up visual inspection and analysis as required for warranty.

Pre-installation Meeting.

Refer to Section [01 31 19 Project Meetings] [insert section number and title].

(Specifier Note:  A Pre-installation meeting is mandatory for projects where the SIGA Products 10 Year Limited Warranty is specified and recommended for all projects using SIGA Majvest® 200. Requirement may be DELETED if SIGA Warranty is not specified).

Convene a pre-installation conference, a minimum of two weeks prior to start of air barrier installation. Attendees shall include Contractor, Architect, installer, and air barrier manufacturer’s designated field representative.

Review all related project requirements and submittals, status of substrate work and preparation, areas of potential conflict and interface, availability of air  barrier system materials and components, installer’s training requirements, equipment, facilities and scaffolding. Coordinate methods, procedures and sequencing requirements for full and proper installation, integration and protection.

Review requirements for sequencing of installation of air barrier system with installation of windows, doors, louvers and metal flashings to provide a air-tight barrier system. Schedule installation of exterior cladding within three months of air barrier system installation.

DELIVERY, STORAGE, AND HANDLING.

Refer to Section [01 60 00 Product Requirements] [insert section number and title].

Deliver air barrier materials and components in manufacturer’s original, unopened, undamaged containers with identification labels intact.

Store air barrier materials and accesories  as recommended by air barrier manufacturer. Storage time is unlimited.  Store in a cool dry place, in the product’s original packaging.

WARRANTY.

Manufacturer Warranty: Submit manufacturer’s standard 10-year warranty for air barrier against defects in materials.

PRODUCTS

- (Specifier Note: Product Information is proprietary to SIGA Majvest® 200. If additional products are required for competitive procurement, add them here).

MANUFACTURER

        - Manufacturer, Basis-of-Design: SIGA Canada Inc., 630 René-Lévesque Blvd. West Suite 2800, Montreal QC  H3B 1S6; +1-855-733-7442; www.siga.swiss.

MATERIAL

Basis of Design : SIGA Majvest 200 , an Air and Water-Resistive Barrier Mechanically Attached

          - 3 layer, spun-bonded polypropylene (PP), non-woven, thermally bonded to a highly vapor permeable, watertight polymeric middle layer

Performance Characteristics.

          - Air leakage:

            - ASTM E2178 : Pass

            - ASTM E2357: Pass

            - CAN/ULC S741-08: Pass

            - CAN/ULC-S742-11: Classification A1

          - Water Vapor Transmission (ASTM E96) :

            - Method A/ desiccant method: 54 US perms (3095 Ng/Pa.m².s)

            - Method B/ water method: 68 US perms (3890 Ng/Pa.m².s)

          - Water Penetration Resistance (AATCC TM127):  >110 inches (>290 cm) when tested in accordance with AATCC Test Method 127.

          - Basis Weight:  0.45 oz/ft² (136 g/m²)

          - Thickness : 0.02" (0.5 mm)

          - Tensile Strength (ASTM D882):

            - 34 lbs/inch MD

            - 24 lbs/inch CD

          - Surface Burning Characteristics (ASTM E 84):

            - Flame Spread: 5 (Class A)

            - Smoke Developed: 50 (Class A)

ACCESSORIES

Joint Tape: Pressure sensitive, with acrylic based adhesive.

SIGA Wigluv® 2.4” (60mm), or wider  4” (100mm), 6” (150mm) , 9”(230mm).

Fasteners

- (Specifier Note:  Fasteners are dependent upon substrate construction.  More than one type of fastener may be required on a single project, REVIEW construction conditions and DELETE fasteners that are unnecessary).

(Specifier Note:  Recommended Fasteners for Steel Frame construction) 1 ¼  inch galvanized or corrosion-resistant screws with caps or gasketed metal washers.

AND/OR

(Specifier Note:  Recommended Fasteners for Wood, Insulated Sheathing Board, Exterior Gypsum ).

Galvanized or corrosion-resistant nails with caps or gasketed metal washers.

Plastic cap staples.

AND/OR

(Specifier Note:  Recommended Fastening to Masonry) 1 ¾ inch (44 mm) minimum Masonry tap-con fasteners with caps or gasketed metal washers.

Flashing

- (Specifier Note:  Flashing is dependent upon construction conditions.  DELETE flashing products that are unnecessary and inappropriate for specific project).

SIGA Wigluv 2.4” (60mm), or wider  4” (100mm), 6” (150mm) , 9”(230mm): Flexible membrane flashing materials for window openings and penetrations, base joint connections, and at transitions between different assembly materials.

AND/OR

SIGA Wigluv 0.75”/1.5” (20/40mm) : Flexible membrane flashing materials for window and door frames and angled penetrations.

AND/OR

SIGA Fentrim® IS 20 2.9” (75mm), or wider 3.9” (100mm) : Pre-folded tape for sealing windows and doors, for indoor application.

Sealants.

- (Specifier Note: Sealants are not required with the SIGA system, but they could be recommended by the window manufacturer. If required by others, sealants must be chemically compatible with the air barrier assembly and may be specified in this Section or under the Division 07 sealants Section. Contact SIGA applications advisor for chemical compatibility list.)

SIGA Meltell® 300,  10.5oz (310ml)  cartbridge,  or Sausages 20.3 (600ml) : A 1-component hybrid polymer-based sealant, sealant for use in facades in interior and exterior above grade applications.

Color : white , black , grey

AND/OR

          - Provide sealant for penetrations as recommended by manufacturer and as specified under Division 07 Section: Sealants.

Compatible with sheet air barrier, roofing and waterproofing membranes and substrate.

Primer.

(Specifier Note:  Product listed below is only recommended for inclusion when required, and should be EDITED for specific project. When using SIGA Wigluv®, primer will be required in concrete, masonry, plaster and softboards applications. For the correct choise of product for the intended application, the substrate matrix, the application recommendations and product information in the SIGA manual must be considered. The currently valid SIGA manual is available at www.siga.swiss).

Provide flashing manufacturer recommended primer to assist in adhesion between substrate and flashing.

Product:

SIGA Dockskin® 100. A water-based, solvent-free, acrylate-copolymer dispersion adhesive for strengthening sandy and fibrous substrates

EXECUTION

EXAMINATION

Verify substrate and surface conditions are in accordance with air barrier manufacturer recommended tolerances prior to installation of air barrier and accessories.

Verify that surfaces and conditions are suitable prior to commencing work of this section.  Do not proceed with installation until unsatisfactory conditions have been corrected.

Verify substrate is dry.

Ensure that the following conditions are met:

Surfaces are sound, dry, even, and free of excess mortar or other contaminants.

Inspect surfaces to be smooth without large voids or sharp protrusions.  Inform General Contractor if substrates are not acceptable and need to be repaired by another sub-contractor.

Inspect masonry joints to be  flush and completely filled, and ensure all excess mortar sitting on masonry ties has been removed. Inform General Contractor if masonry joints are not acceptable and need to be repaired by the masonry sub-trade.

Verify sealants are compatible with flexible sheet air barrier proposed for use. The current valid SIGA sealant compatibility matrix is available at www.siga.swiss

Notify Architect in writing of anticipated problems installing the air barrier material over substrate prior to proceeding.

INSTALLATION- AIR BARRIER

Install air barrier over exterior face of exterior wall substrate in accordance with manufacturer recommendations.

Install air barrier prior to installation of windows and doors.

Begin by aligning the bottom edge of the roll approximately 3-6 inches below the base of the wall onto the foundation, approximately 12 inches from a corner, with the print side facing out.  Maintain air barrier plumb and level.

Unroll the  air barrier completely, wrapping the entire building, including door and window openings.

Temporarily fasten every 24" - 36" within coverage area.

Overlap air barrier at all corners of building by a minimum of 12 inches.

Overlap air barrier at all seams by a minimum of 4 inches and tape all horizontal and vertical seams with SIGA Wigluv®.

Secure to foundation with SIGA Wigluv with primer SIGA Dockskin® 100 , as recommended by air barrier manufacturer.

Air Barrier permanent Attachment: Fasten securely to a stud, structural sheathing or through insulation board to an underlying framing member with maximum horizontal and vertical spacing of 24”.

- (Specifier Note:  Attachment method is dependent upon substrate construction.  DELETE methods that are unnecessary and inappropriate for specific project).

(Specifier Note:  Steel or Wood Frame Construction) Attach air barrier to studs through exterior sheathing. Secure using air barrier manufacturer recommend fasteners, space 24 inches on center, maximum horizontally.

AND/OR

(Specifier Note:  Masonry Construction) Attach air barrier to masonry. Secure using air barrier manufacturer recommend fasteners, space 24 inches maximum horizontally. Air barrier may be temporarily attached to masonry using recommended adhesive, placed in vertical strips spaced 24 inches on center, when coordinated on the project site.

- (Specifier Note: Cladding anchors, supports and fasteners will likely be specified in the section including the cladding, COORDINATE the inclusion of the following paragraph in the appropriate specification section. With air barrier manufacturer’s approval cladding anchors can be used to fasten the air barrier).

Apply a piece of SIGA Wigluv or air barrier manufacturer approved alternate to air barrier membrane prior to the installation cladding anchors.

SEAMING

Seal seams of air barrier with seam tape SIGA Wigluv 2.4” (60mm) or wider ,  at all vertical and horizontal overlapping seams.

Seal any tears or cuts with seam tape SIGA Wigluv as recommended by air barrier manufacturer.

- (Specifier Note: Opening preparation and flashing installation is dependent upon the construction of the opening and construction of the window. DELETE execution requirements that are not appropriate for specific project. COORDINATE proper design and detailing at windows, doors and other openings or intersections for proper flashing in accordance with window manufacturer guidelines, industry standards and best flashing and waterproofing practices).

      - OPENING PREPARATION (for all windows)

- (Specifier Note: Window manufacturer’s instructions over-ride SIGA specifications for window openings. The installer is responsible to resolve any conflicts in the specifications, sequencing, materials or techniques between window manufacturer’s instructions and SIGA specifications before construction. MAINTAIN the following opening preparation and flashing articles, when used in conjunction with non-flanged windows, or flanged windows. Contact SIGA applications advisor for assistance and consult the SIGA Guidelines www.siga.swiss).

        - Membrane preparation

          - Cut SIGA Majvest® 200 flush with sill and jambs, and 1" above the head

          - Create a flap of SIGA Majvest 200  above RO head. From each upper corner make a 9" cut upward at 45 degrees. Flap the top piece of SIGA Majvest 200  to the outside and temporarily hold it up with a piece of tape.

        - Sill preparation

          - Cut SIGA Wigluv® 4" wider than the sill so it will extend 2" past each end of the rough opening.

          - Crease the tape using the split backing and remove one backing strip. Center and apply to exterior face.

          - Cut tape lengthwise toward corners.

          - Remove second backing strip and apply tape on sill. Firmly press the tape on with a roller or squeegee.

- (Specifier Note: Best construction practice requires window sill details to be waterproofed and flashed prior to the placement of the window assembly. DELETE methods that are unnecessary and inappropriate for specific project).

- (Specifier Note: no pan flashing for all construction details incorporating fenestration drainage systems  provided by the building designer, or where wall construction details are specifically provided by fenestration manufacturers’ installation instructions.) Cover horizontal sill by aligning SIGA Wigluv with inside edge of sill.  Release one backing strip and adhere to rough opening across sill.  Release remaining backing strip and secure flashing firmly to wall face.

OR

- (Specifier Note: pre-fabricated sill pan flashing) Follow sill pan manufacturers’ instructions, window manufacturer’s instructions and ASTM E2112 recommendations.

- OR

- (Specifier Note: field-fabricated sill pan flashing ) Use SIGA Wigluv  to field-fabricate a sloped sill pan flashing over a beveled slope-to-drain sill plate or over sill with back-dam. Cover horizontal sill by aligning SIGA Wigluv with inside edge of sill.  Release one backing strip and adhere to pan flashing across sill.  Release remaining backing strip and secure flashing firmly to wall face.

        - Corner preparation

          - Create two gussets with SIGA Wigluv  100 by cutting a piece of tape that’s the full depth of the rough opening plus 3”.

          - Cut one end of the tape at a 45 degree angle to create a “dog ear”.

          - Crease tape lengthwise, fold in the middle and work gusset into corner while removing one backing strip.

          - Firmly press the tape onto the rough opening using a roller or squeegee.

          - Stretch the SIGA Wigluv  tape around the corner toward the ecterior – wrinkles are normal.

        - Repeat steps C and D for remaining portions of the rough opening (jambs and head) and corners.

        - Coordinate flashing with window installation.

      - FLASHING (for use with non-flanged windows)

- (Specifier Note: Refer to section 3.4 Opening Preparation [above] before installing the window according to manufacturer’s instructions).

        - Install window according to manufacturer’s instructions.

        - Sill preparation

          - OPTIONAL Dependent on window type the sill can either be taped or left open for drainage. Check with your window manufacturer before taping.

          - Cut SIGA Wigluv®  20/40 about 2" wider than the width of the prepared rough opening. Remove smaller backing paper and apply tape along the underside of the window while applying firm pressure.

          - Remove larger backing paper and press on firmly using a roller or squeegee.

          - Make 45° cuts at each end, from the inside corner outward, make sure to not cut tape too deep to avoid pinholes. Fold both ends up and apply firm pressure.

        - Jamb preparation

          - Cut SIGA Wigluv  20/40 or about 2" longer than the vertical portion of the rough opening. Remove smaller backing paper and apply vertical layer of tape along the window frame while applying firm pressure.

          - Remove larger backing paper and press on firmly while using a roller or squeegee. Make 45° cuts at each end, from the inside corner outward, make sure to not cut tape too deep to avoid pinholes. Fold both ends up and apply firm pressure. Repeat on both sides.

        - Head preparation

          - Cut SIGA Wigluv  20/40 or about 4" wider than the width of the prepared rough opening so both ends are overlapping the tape on the jamb. Remove smaller backing paper and apply SIGA Wigluv  20/40 along the top of the window while applying firm pressure.

          - Remove larger backing paper and press on firmly using a roller or squeegee. Make 45° cuts at each end, from the inside corner outward, make sure to not cut tape too deep to avoid pinholes. Fold both ends up and apply firm pressure.

        - Interior Air-Seal

          - Before sealing the interior, insulation must be used around the perimeter of the window in accordance with shop drawings and the insulation manufacturer’s guidelines. Insulation must allow for expansion and contraction of the installed window.

          - Apply SIGA Fentrim® IS 20 directly on window frame with the pre folded section. Remove backing paper and apply firm pressure using a roller or squeegee. Apply SIGA Fentrim IS 20 along all sections of the window right up to the corner.

          - Create corner piece and place into corners. Repeat step for all 4 corners.

          - Tape around the interior face of the window, and seal the mounting brackets or any other possible sources of leakage.

          - Ensure a minimum 1” (25mm) overlap with SIGA Fentrim IS 20 in every direction.

      - FLASHING (for use with flanged windows)

- (Specifier Note: Refer to section 3.4 Opening Preparation [above] before installing the window according to manufacturer’s instructions).

        - Install window according to manufacturer’s instructions.

        - Jamb Counterflashing

          - Cut SIGA Wigluv®  (4” or wider) about 2" longer than the vertical portion of the rough opening.

          - Remove smaller backing paper and apply vertical layer of tape along the window frame while applying firm pressure.

        - Head Counterflashing

          - Cut SIGA Wigluv  (4” or wider) about 4" wider than the width of the prepared rough opening so both ends are overlapping the tape on the jamb.

          - Remove smaller backing paper and apply tape along the top of the window while applying firm pressure.

        - Membrane Integration

          - Position air barrier head flap across head flashing. Adhere using 4-inch wide SIGA Wigluv  over the 45-degree seams.

          - Tape head flap in accordance with manufacturer recommendations.

        - Wall assemblies containing a vapor retarder on the interior wall assembly:

          - Extend flashing into rough opening to ensure sufficient membrane for connection with vapor retarder and provide a continuous air barrier assembly.

          - Before sealing  the interior, insulation must be used around the perimeter of the window in accordance with shop drawings and the insulation manufacturer’s guidelines. Insulation must allow for expansion and contraction of the installed window.

        - Interior Air-seal

          - Before sealing the interior, insulation must be used around the perimeter of the window in accordance with shop drawings and the insulation manufacturer’s guidelines. Insulation must allow for expansion and contraction of the installed window.

          - Apply SIGA Fentrim® IS 20 directly on window frame with the pre folded section. Remove backing paper and apply firm pressure using a roller or squeegee. Apply SIGA Fentrim  IS 20 along all sections of the window right up to the corner.

          - Create corner piece and place into corners. Repeat step for all 4 corners.

          - Tape around the interior face of the window, and seal the mounting brackets or any other possible sources of leakage.

          - Ensure a minimum 1” (25mm) overlap with SIGA Fentrim IS 20 in every direction.

PENETRATIONS

Round or square penetrations  must  be sealed with SIGA Wigluv.

Begin the sealing process at bottom of penetrations, shingling upper tape over bottom tape.

Apply multiple, short pieces of SIGA Wigluv around the penetration to create a gasket.

Products that have flanges should be integrated into the water-resistive barrier using SIGA Wigluv.

WALL TO FOUNDATION TRANSITION

(Specifier Note : When using SIGA Wigluv®, primer will be required in concrete, masonry, plaster and softboards applications. For the correct choise of product for the intended application, the substrate matrix, the application recommendations and product information in the SIGA manual must be considered. The currently valid SIGA manual is available at www.siga.swiss).

Before sealing, clean the substrate. The substrate must be dry, structurally sound and free of any dirt and grease. It must not be adhesive-repellent.

If the intent is to use SIGA Wigluv , bond the base-joint substrate with high-performance primer SIGA Dockskin® . Brush or roll on SIGA Dockskin® 100 primer to concrete, and let it set, clear and tacky.

Align the center of SIGA Wigluv 4“(100mm)  or wider  to the center of the joint, between the concrete base joint and the air barrier SIGA Majvest® 200. Minimum 2” overlap is required onto concrete.

Secure in place, and remove backing strip.

Bond without any tension and wrinkles and press on firmly with hand or roller.

OTHER DETAILING/FLASHING

Contact a SIGA applications advisor for assistance with any unlisted installation details including, but not limited to, the following:

Construction joints

Transitions :

Roof to air barrier.

Air barrier to vertical or horizontal waterproofing.

Fastener penetrations.

Inside and outside corners.

Shelf angles.

Reverse laps.

Complete detailing and flashing installations per Air Barrier Manufacturer’s installation guide, details, and this specification.

FIELD QUALITY CONTROL

Notify air barrier manufacturer’s designated representative to obtain periodic observations of air barrier system installation if required. Notification shall be a minimum of 30 days prior to the start of installation. Notice of final observation shall be made 30 days prior to completion.

Inspections by Commissioner or Architect: Air barrier materials, accessories, and installation are subject to inspection for compliance with performance requirements. Repair damage to air barriers caused by destructive testing; follow manufacturer's written instructions.

PROTECTION AND CLEANING

Protect air barrier from contact with incompatible materials and sealants not approved per air barrier manufacturer’s recommendation.

Protect installed air barrier system from damage during construction prior to cladding installation.

END OF SECTION

DISCLAIMER: SIGA Canada Inc. Guide Specifications have been written as an aid to the professionally qualified Specifier and Design Professional. The use of this Guideline Specification requires the sole professional judgment and expertise of the qualified Specifier and Design Professional to adapt the information to the specific needs for the Building Owner and the Project, to coordinate with their Construction Document Process, and to meet all the applicable building codes, regulations and laws. SIGA Canada Inc. EXPRESSLY DISCLAIMS ANY WARRANTY, EXPRESSED OR IMPLIED, INCLUDING THE WARRANTY OF MERCHANTABILITY OR FITNESS FOR PARTICULAR PURPOSE OF THIS PRODUCT FOR THE PROJECT.